## Slide 1
Dave Butler
Hall D Slow Controls
01100 01100 10010 0000 10010 11111 011011 11010

## Slide 2: Agenda
PLC Overview
RSLogix5000 Software
  Ladder Logic
  Structured Text
  Function Block
Communications
HMI System
Detector Controls
Solenoid Controls/Improvements
Slow Controls Progress

## Slide 3: Programmable Logic Controllers
ControlLogix (1756)
  4 Mbyte memory
  Can be redundant
  Chassis based
    We use 10-slot chassis
CompactLogix (1769)
  1.5 Mbyte memory
  No redundancy available
  No chassis
    L35E Controllers can talk to 32 I/O Modules
Power
Supply
Controller
Chassis
Comm
Controller
Power
Supply
I/O Modules

## Slide 4: I/O (Local vs Remote)
Local I/O
  Any modules in the same chassis as the controller
Remote I/O
  Modules NOT in the same chassis as the controller
  Can be Point IO
    Point IO is available for ControlLogix and CompactLogix
Solenoid Controls
Controller
Comm
Local
Remote

## Slide 5: Point IO (always remote)
Modular IO modules
  Ideal for mounting on remote panels where small IO counts are required
  Communicate via any standard protocol
    We use Ethernet/IP
      ControlNet, DeviceNet, Profibus all available
  Snap together on DIN rail
    No chassis required
    24 VDC powered
Communication Module
Output Module

## Slide 6: RSLogix5000 Software
Ladder Logic

## Slide 7: RSLogix5000 Software
Structured Text

## Slide 8: RSLogix5000 Software
Function Block

## Slide 9: Communications
All Allen Bradley equipment networked with Ethernet/IP
  Uses standard CC-configured Ethernet hardware (switches, cables, etc)
  Proven to be very reliable
  Three methods for PLC to PLC connections
    Produced/Consumed Tags
    Messages
    EPICS (reads from one and writes to another)
Serial Communications (RS232, RS485, TCP) use a Real Time Automation gateway
  435NBX for RS232/485 to PLC
  490NBX for TCP to PLC

## Slide 10: Human Machine Interface (HMI)
Networked applications provide many services
  FactoryTalk View Studio
    Create HMI screens and manage HMI application
      Datalogging
      Screen prints for auto log-entry
      Create & manage RSLinx Enterprise FactoryTalk View SE
    Client for viewing HMI displays
  FactoryTalk Network Directory Server
    Backbone of FactoryTalk Network – directs client computers to servers
  FactoryTalk HMI Server
    Hosts HMI screens to be served to clients
    Can be redundant (requires another HMI license)
  RSLinx Enterprise
    Gathers tag data from the PLC for display in the HMI
    Can be redundant (does not require additional licensing)
    Alarms and Events (screen alarms)
      *Alarm pages come from PLC and are independent of the PC’s running the Alarms and Events services

## Slide 11: Solenoid Test HMI Schematic
halldsc6
halldsc7
halldsc8
Network Directory Server
HMI Server
FactoryTalk View Studio
FactoryTalk View SE
ODBC connection to MySQL database (hosted on gluon01)
RSLinx Enterprise Server (Primary)
FactoryTalk View Studio
FactoryTalk View SE
RSLinx Enterprise Server (Redundant)
FactoryTalk View Studio
FactoryTalk View SE
Ethernet
gluon01
MySQL Server for FactoryTalk Datalogging

## Slide 12: Hall Operations HMI Schematic
halldsc8
halldsc7
halldsc6
Network Directory Server
HMI Server
FactoryTalk View Studio
FactoryTalk View SE
ODBC connection to MySQL database (hosted on gluon01)
RSLinx Enterprise Server (Primary)
FactoryTalk View Studio
FactoryTalk View SE
RSLinx Enterprise Server (Redundant)
FactoryTalk View Studio
FactoryTalk View SE
Ethernet
gluon01
MySQL Server for FactoryTalk Datalogging
Hall D
Counting
House
TEDF

## Slide 13: BCAL Controls
Module Qty | Name | PN | Total Channels
1 | Ethernet Processor, 1.5 Mbyte Memory | 1769-L35E | --
1 | Power Supply 120/240 VAC Input | 1769-PA4 | --
16 | 6 Channel RTD /Resistance Input Module | 1769-IR6 | 96
2 | Pressure Transducer | Point I/O | 4
2 | Temperature | Point I/O | 4

## Slide 14: FDC/CDC Controls
Gas Shed:
Qty | Name | PN | Total Channels
1 | 24VDC Ethernet Adapter | 1734-AENT | --
1 | 24 VDC 8 Ch Analog Input | 1734-IE8C | 8
1 | 24 VDC 2 Ch Analog Current Input | 1734-IE2C | 2
1 | 24 VDC 4 Ch Relay Module (NO) | 1734-OW4 | 4
1 | ASCII to PLC Gateway | 435NBX | 2
Qty | Name | PN | Total Channels
1 | Ethernet Processor, 1.5 Mbyte Memory | 1769-L35E | --
1 | Power Supply 120/240 VAC Input | 1769-PA4 | --
3 | 16 Ch Relay Output | 1769-OW16 | 48
1 | 4 Ch Analog Current/Voltage Input | 1769-IF4 | 4
2 | ASCII to PLC Gateway (PR 327905) | 435NBX | 4
3 | Chiller (FDC/BCAL) | RS485 | 1
2 | Thermocouples (CDC) | 1769-IT6 | 12
Hall D:

## Slide 16: Target/Start Counter Controls
Qty | Sensory Name | Signal Type
1 | H2 Supply Pressure | 4-20 mA
1 | H2 Return Pressure | 4-20 mA
1 | Coarse Vacuum Gauge | 0-10 V
1 | High Vacuum Gauge | 1-9 V
1 | Lakeshore 336 | TCP
1 | Lakeshore 218 | RS232
1 | PTR Compressor | RS232
3 | Relay | Relay Contact
Qty | Name | PN | Total Channels
1 | TCP to ControlLogix Gateway (in 2012) | 490NBX | --
1 | Ethernet Processor, 1.5 Mbyte Memory | 1769-L35E | --
1 | Power Supply 120/240 VAC Input | 1769-PA4 | --
1 | 8 Ch Analog Input Module | 1769-IF8 | 8
1 | 16 Ch 24 VDC Sinking/Sourcing Input | 1769-IQ16 | 16
1 | ASCII to CompactLogix Gateway PR#327842 | 435NBX | 2
2 | 6 Channel Thermocouple Modules | AB1769IT6 | 12
Layout
Ethernet
CompactLogix
490NBX
LakeShore 336
435NBX
LakeShore 218
RS232
PTR Compressor
L35
PA4
IF8
IQ16
OW16
IT6
IT6

## Slide 17: FCAL / Pair Spectrometer Control
Qty | Sensory Name | Signal Type
2 | Magnetic Door Lock Power | Relay Out
2 | Temperature | Analog In
2 | Humidity Sensor | Analog In
4 | Photosensor | Analog In
1 | Crash Button | Digital In
1 | Outer Door Button | Digital In
1 | Inner Door Button | Digital In
1 | PMT Base Power Relay | Relay Out
1 | Trip Switch for Fault Reset | Digital In
4 | Thermocouples (PS) | Thermocouple In
Qty | Name | PN | Total Channels
1 | Ethernet Processor, 1.5 Mbyte Memory | 1769-L35E | --
1 | Power Supply 120/240 VAC Input | 1769-PA4 | --
1 | 16 Channel AC/DC Relay Module | 1769-OW16 | 16
1 | 16 Channel 24 VDC sink/source Input | 1769-IQ16 | 16
1 | 8 Channel Voltage/Current Analog Input | 1769-IF8 | 8

## Slide 18: Solenoid Controls
Solenoid Analog/Digital
Controls
(Strain, Valves, Temp, etc)
Chassis 0
Chassis 1
Chassis 2
Chassis 3
Valve 6
Vacuum Chassis
LakeShore 1 & 2
LakeShore 3 & Mass Flow
Danfysik
Ethernet
RS232
RS232
RS232
435NBX1
435NBX2
435NBX3
AENT1
AENT3
EN2T1
EN2T2
EN2T3
EN2T4
halldsc6
halldsc7
halldsc8
Windows PC’s:
Programming Terminal
HMI Services
Datalogging (logs exist on gluon01)
Alarms & Events
EPICS
Archiving
HMI Displays
Alarms

## Slide 19: Solenoid Controls Improvements
Upgraded the Software Quench Detectors
  Added dynamic Current vs Inductance calculation
  Added a 200ms timer to eliminate erroneous trips
  Integrated the PXI watchdog timer into the software Quench detector
Solenoid Current vs Bath Pressure
Ramp Profiles

## Slide 20
Chart: Inductance vs Current
| 0 | 250 | 500 | 750 | 1000 | 1250 | 1500
Inductance vs Current | 28.0016 | 27.7453 | 27.3745 | 26.8893 | 26.2897 | 25.5756 | 24.7472
Notes: Each voltage tap has and individual curve applied and for the 3 Channel QD the were summed

## Slide 21: Solenoid Current vs Bath Pressure

## Slide 22: Slow Controls Progress
 | Order Hardware | Assemble Hardware | Installed In Hall | Code | Cabling | Testing/Debug | Commissioning
Solenoid | 100% | 100% | No | 90% | 0% | 90% | 90%
FCAL/PS | 100% | 100% | Yes | 90% | 50% | 0% | 0%
FDC/CDC | 100% | 80% | No | 10% | 0% | 0% | 0%
BCAL US | 100% | 90% | No | 80% | 20% | 0% | 0%
BCAL DS | 100% | 90% | No | 80% | 10% | 0% | 0%
Target/Start Counter | 100% | 100% | No | 10% | 0% | 0% | 0%

## Slide 23: Questions?
Rhetorical
Coffee waiting
It’s been a long day
Do you need to stretch you’re legs?
Rhetorical
It’s been a long day
Coffee waiting
Rhetorical
Rhetorical
Coffee waiting
It’s been a long day
Do you need to stretch you’re legs?
It’s been a long day
Rhetorical