## Slide 1: UPS for Hall D
During two month collected requirements for Hall D UPS
Included requirements from
  Dave Butler for CompactLogix
  Requirements for network switches
  Requirements for motion controller for TAC
  Requirement for solenoid (ControlLogix chassis and valves only)
Will require 62 Amps
  One option
    2x 20Amps circuits on north side
    2x 20Amps circuits on south side
  Joe Beaufait will figure out how to run circuit
Hall D will need 3KW of power for 20 minutes after power loss to park in a safe stage
I will send these requirements to Joe Beaufait Friday morning.
"C:\Program Files (x86)\W-IE-NE-R\MUSEcontrol\MUSEcontrol.exe" USB 0x224