## Slide 1: Solenoid PLC Update: Summer 2016 (ongoing)

## Slide 2: Solenoid Clock Sync
ntp1.jlab.org
halldeweb1
1756 Controller
“wallclock”
MPS Comms Routine
SOE
1756-EWEB(halldeweb1) module gets time from ntp1.jlab.org, one minute update interval
Halldeweb1 then propagates NTP time to solenoid controller “wall clock”
Controller “wallclock” propagates through all solenoid PLC chassis
Set clock command inserted into the PLC to Danfysik ASCII commands. Update interval ~4 hours

## Slide 3: Solenoid Clock Sync, continued
Problem: Ethernet/ASCII comms to set clock.
  The command must be processed in PLC, sent to Ethernet module, sent to NBX module, converted to ASCII, then sent and processed by Danfysik
Solenoid PLC controller
Solenoid Ethernet module
NBX435 Module
Danfysik
Proposed Solution: Simulate PLC SOE time stamp and Danfysik ‘first’ time stamp from all MPS/SOE common interlocks to calculate the average processing time. Use that average time to offset the actual time being sent to the Danfysik.
  Lots of assumptions, time can only be offset by 1 second resolution
  Is it necessary? We will play with this process but don’t have to implement an offset as long as the delay is known… Cannot try until early august

## Slide 4: Mass Flow Calculations
Problem: Mass flow program calculated VCL flow based on last received ASCII current reading from Danyfisyk. If communications is lost(like when fuse blows) the VCL flow does not update in case of dump/current change.
Solution: Mass flow program now will change the current source to PXI current in situations when the ASCII current reading is not updating, it will switch back once it starts updating again.
It might be better to keep the mass flow program on PXI current? Thoughts/suggestions welcome…