## Slide 1: BCAL Interlock System
US BCAL Chiller
US BCAL MPOD 1
US BCAL PLC
Pulsed Output from Flow meter to PLC
From US BCAL cooling loop
US BCAL MPOD 1
RS485 from Chiller
To PLC
DS BCAL Chiller
DS BCAL MPOD 1
DS BCAL PLC
Pulsed Output from Flow meter to PLC
From DS BCAL cooling loop
DS BCAL MPOD 2
RS485 from Chiller
To PLC
The flow meters act as a failsafe in case the RS485 serial communication fails
The PLC can use flow data and RTD temperature data to determine if the low voltage should be turned off
5V TTL
5V TTL
PLC Remote On/Off 24V
PLC Remote On/Off 24V

## Slide 2: BCAL Interlock System
US BCAL MPOD 1
US BCAL PLC 24V Output
US BCAL MPOD 1
5V TTL
Relay
5 Volt Power Supply
Relay
5V TTL
There is no Point IO module that puts out 5V with enough current (5ma) to enable the MPOD
The PLC can use flow data and RTD temperature data to determine if the low voltage should be turned off

## Slide 3: BCAL Interlock System

## Slide 4: BCAL Interlock System

## Slide 5: BCAL Interlock System